## 00 Load Summary
Project Name & Location | Lodha Asode-C3 , Thane |  | Doc.Ref No. | ELE-LOS-001
Client | Lodha |  | Initial Date | 2023-10-09
PMC |  |  | Rev No. | R0
Architect | Proconvis Consultants Pvt.Ltd |  | Prepared By | Kartheeswaran
M & E Consultant | Innowell Engineering International Pvt. Ltd |  | Reviewed By | Avinash
Document | Electrical Load |  | Approved By | Selvakumar
Service | Electrical
S.No | Description | Toatal Area (Sq.ft) | Total Connected Load (kW) | Total Demand Load (kW)
1 | Block C3 | 217863.36 | 220.055 | 173.755
Total Load |  |  | 220.055 | 173.755
A. | TRANSFORMER SIZING FOR BLOCK-C3
| Maximum Demand Load @ 0.90 |  | 156.3795 | kW
| With Power Factor of 0.8, demand in kVA |  | 195.4744 | kVA
| Transformer with 80% loading factor |  | 245 | kVA
Hence we recommend 1 Nos 250kVA Transformer (Oil type) as per MSEDCL
B. | DG SET SIZING FOR BLOCK-C3 (PROVISION)
| Maximum Demand Load @ 0.90 |  | 156.3795 | kW
| With Power Factor of 0.8, demand in kVA |  | 195.4744 | kVA
| Loading on Diesel Generator 85% |  | 229.9699 | kVA
Hence we recommend 1 Nos 250kVA Acoustic DG

## Block-C3
Project Name & Location | Lodha Ascode-C3 , Thane |  |  |  |  | Doc.Ref No. | ELE-LOS-02
Client | Lodha |  |  |  |  | Initial Date | 2023-10-09
PMC | [5 empty] | Rev No. | R0
Architect | Proconvis Consultants Pvt.Ltd |  |  |  |  | Prepared By | Kartheeswaran
M & E Consultant | Innowell Engineering International Pvt. Ltd |  |  |  |  | Reviewed By | Avinash
Document | Electrical Load |  |  |  |  | Approved By | Selvakumar
Service | Electrical
SNO | DESCRIPTION | QTY | Area (Sq.ft) | (Lighting/Power Wattage in kW) | Total Connected Load (kW) | Div | Dem.Load (kW)
1 | Power Load (Tenant Load) |  | 217863.36 |  | 201 | 0.8 | 160.8
2 | HVAC Load |  |  | 5 | 5 | 0.8 | 4
3 | ELV Load |  |  | 1.305 | 1.305 | 1 | 1.305
4 | Rolling shutter | 17 |  | 0.75 | 12.75 | 0.6 | 7.65
Total |  |  |  |  | 220.055 |  | 173.755
217.1938
[5 empty] | 217 | Kva
[5 empty] | 16.1937 | KVA
200.8063
160.645

## ELV & EMG Lighting Load
Project Name & Location | Lodha Ascode-C3 , Thane |  |  |  | Doc.Ref No. | ELE-LOS-03
Client | Lodha |  |  |  | Initial Date | 2023-10-09
PMC |  |  |  |  | Rev No. | R0
Architect | Proconvis Consultants Pvt.Ltd |  |  |  | Prepared By | Kartheeswaran
M & E Consultant | Innowell Engineering International Pvt. Ltd |  |  |  | Reviewed By | Avinash
Document | Electrical Load |  |  |  | Approved By | Selvakumar
Service | Electrical
SNO | Description | Load per Equipment (kW) | Number of Equipment | Connected Load in kW | Diversity Factor | Total MD in kW
Sl No. | Description | Load per Equipment (kW) | Number of Equipment | Connected Load in kW | Diversity Factor | Total MD in kW
BLOCK-C3
1 | Fire alarm panel | 0.3 | 1 | 0.3 | 1 | 0.3
2 | Power supply unit - Hooter | 0.14 | 4 | 0.56 | 1 | 0.56
3 | Power supply - Beam Detector | 0.14 | 3 | 0.42 | 1 | 0.42
4 | Exit Signages | 0.001 | 25 | 0.025 | 1 | 0.025
Total load |  |  |  | 1.305 |  | 1.305